| Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 機櫃/Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack |
| PDU Power Available | N/A | No | No | Dashboard shows PDU source, trend unknown | No | Yes | No | N/A | No | N/A | N/A | N/A | N/A |
| CPU Count | 1 | 1 | 2 | 2 | No | 2 | No | 1 | No | No | 2 | 2 | 2 |
| CPU Model | AMD EPYC 9354 32-Core Processor | Intel(R) Xeon(R) Gold 6433N | Intel(R) Xeon(R) Gold 6226R CPU @ 2.90GHz *2 | Intel(R) Xeon(R) Gold 6326 CPU @ 2.90GHz*2 | No | Intel(R) Xeon(R) CPU E5-2695 v4 @ 2.10GHz*2 | No | Intel(R) Xeon(R) Gold 6433N | No | No | Intel Xeon processor*2 | Intel(R) Xeon(R) Gold 6326 CPU @ 2.90GHz*2 | Intel(R) Xeon(R) Gold 6226R CPU @ 2.90GHz |
| CPU Temp Available | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes |
| Memory Available | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | Yes | Yes | Yes |
| Storage Available | Yes | N/A | Yes | Yes | No | No | No | N/a | No | No | Partial | Yes | Yes |
| Network Available | Yes | Yes | Partial | Partial | No | Yes | No | N/a | No | No | Yes | Partial | Partial |
| Redfish Power Available | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | N/a | Yes | Yes |
| PSU Available | Yes | Yes | Yes | Yes | No | Yes | No | Yes | No | No | N/a | Yes | Yes |
| Fan RPM Available | Yes(1~8) | Yes(1~5) | Yes(1~6) | Yes(1~6) | No | Yes | No | Yes(1~3) | No | No | N/a | Yes(1-6) | Yes |
| Inlet Temp Available | Yes | No | Yes | Yes | No | No | No | N/a | No | No | N/a | Yes( | Yes |
| Outlet Temp Available | No | No | No | Yes | No | No | No | No | No | No | N/a | Yes | Yes |

- Sever資源總表

黃色底: 主要採用的類別

紅色底:  CortexDC沒有資料

- Sever 基本資訊

| Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 機櫃/Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW New-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack | BMW Old-Rack |
| 廠牌/Vendor | Supermicro | Supermicro | HPE | Dell Inc. | N/A | Supermicro | N/A | Supermicro | N/A | N/A | Intel Corporation | Dell Inc. | Dell Inc. |
| Model | AS-1115HS-TNR | SYS-111E-WR | ProLiant DL380 Gen10 | PowerEdge R750 | N/A | SSG-6028R-E1CR12L | N/A | SYS-521E-WR | N/A | N/A | S2600WFT | PowerEdge R750 | PowerEdge R740 |
| 序號/Serial Number | A515042X5816356 | A497720X4813116 | SGH146Y31S | CNIVC0029B0942 | N/A | A17487427611634 | N/A | A497706X4200296 | N/A | N/A | WO152116L01S001 | CNFCP0032L00VK | CNIVC0022P2057 |
| U Position | U18-U18 | U22-U22 | U28-U29 | U31-U32 | U37-U38 | U8-U9 | U12-U13 | U15-U16 | U23-U24 | U31-U32 | U33-U34 | U35-U36 | U37-U38 |
| IP | 192.168.10.81 | 192.168.10.87 | 192.168.10.125 | 192.168.8.222 | 192.168.10.128 | 192.168.10.88 | 192.168.10.74 | 192.168.10.92 | 192.168.10.121 | 192.168.10.94 | 192.168.10.75 | 192.168.10.123 | 192.168.10.124 |
| Online Status | Online | Online | Online | Online | Offline | Online | Offline | Online | Offline | Offline | Online | Online | Online |
| Redfish Configured | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |
| Redfish Data Available | Yes | Yes | Yes | Yes | No/Offline | Yes | No | Yes | No | No | Yes | Yes | Yes |
| Redfish power(server-level) | Yes | Yes | Yes | Yes | N/A | Yes | N/A | Yes | N/A | N/A | N/A | Yes | Yes |
| Node Exporter Configured | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | N/A | N/A | Yes | Yes | Yes |
| Node Exporter Data Available | Partial | Partial | Partial | Partial | No | Yes | No | Partial | NO | No | NO | Yes | Not checked |
| PDU Name | PDU [Raritan] PX4-5256CR-C8E8A0 | No outlet mapping shown | No outlet mapping shown | PDU [Raritan] PX4-5256CR-C8E8A0 | No outlet mapping shown | PDU [Raritan] PX4-5256CR-C8E8A0 | No | PDU [Raritan] PX4-5256CR-C8E8A0 | No | PDU [Raritan] PX4-5256CR-C8E8A0 | PDU [Raritan] PX4-5256CR-C8E8A0 | PDU [Raritan] PX4-5256CR-C8E8A0 | PDU [Raritan] PX4-5256CR-C8E8A0 |
| PDU Relationship | Yes | No | No | Yes | No | Yes(Power relationship in topology) | No | Yes | No | Yes | Yes | Yes | Yes |
| PDU Outlet | Outlet 5 | Unknown | Unknown | Outlet 12 | Unknown | Outlet 9 | Unknown | Outlet 11 | Unknown | Outlet 4 | Outlet 8 | Outlet 6 | Outlet 10 |
| Health Status Available | Yes | Yes | Yes | Yes | no | Yes | no | Yes | Yes | Yes | Yes | Yes | Yes |
| Research Usability | High | Medium | Medium | High | Low | High | Low | High | Low | Low | Medium | High | High |

- Sever sensor(System Board)

| Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Inlet Temp(limit:45) | PCH Temp(limit:90) | P1 DIMM 1-6 (limit:90) | System Board Inlet Temp(limit:42) | N/a |  | N/a | PCH Temp(limit:90) | N/a | N/a | N/a | limited:42 | limited:47 |
| 2 | System Tepm(limit:85) | System Tepm(limit:85) | P1 DIMM 7-12 (limit:90) | System Board Exhaust Temp(limit:80) | N/a |  | N/a | System Temp(limit:85) | N/a | N/a | N/a | System Board Inlet Temp | System Board Inlet Temp |
| 3 | Peripheral Temp(limit:85) | Peripheral Temp(limit:85) | P2 DIMM 1-6(limit:90) |  | N/a |  | N/a | Peripheral Temp(limit:85) | N/a | N/a | N/a | System Board Exhaust Temp | System Board Exhaust Temp |
| 4 | SOC_VRM Temp(limit:100) |  | P2 DIMM 7-12(limit:90) |  | N/a |  | N/a |  | N/a | N/a | N/a |  |  |
| 5 | VDDIO_VRM Temp(limit:100) |  | HD Max(limit:60) |  | N/a |  | N/a |  | N/a | N/a | N/a |  |  |
| 6 | P1V1_VRM Temp(limit:100) |  | Stor Batt 1(limit:60) |  | N/a |  | N/a |  | N/a | N/a | N/a |  |  |
| 7 |  |  | VR P1(limit:115) |  | N/a |  | N/a |  | N/a | N/a | N/a |  |  |
| 8 |  |  | VR P1 Mem 1(limit:115) |  | N/a |  | N/a |  | N/a | N/a | N/a |  |  |
| 9 |  |  | VR P1 Mem 2(limit:115) |  | N/a |  | N/a |  | N/a | N/a | N/a |  |  |
| 10 |  |  | VR P2 Mem 1(limit:115) |  | N/a |  | N/a |  | N/a | N/a | N/a |  |  |
| 11 |  |  | VR P2 Mem 2(limit:115) |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  | Chipset(limit:100) |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  | BMC(limit:110) |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  | BMC Zone(limit:90) |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  | HD Controller(limit: 100) |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  | HD Cntlr Zone(limit:85) |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  | LOM Card Zone(limit:75) |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  | PCI 1(limit:100) |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  | PCI 1 Zone(limit:75) |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  | PCI 2 Zone(limit:75) |  |  |  |  |  |  |  |  |  |  |
| 21 |  |  | PCI 3 Zone(limit:75) |  |  |  |  |  |  |  |  |  |  |
| 22 |  |  | Battery Zone(limit:75) |  |  |  |  |  |  |  |  |  |  |

- Server sensor(memory)

| Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| limit temp | limit:85 | limit:86 |  |  |  | limit:85 |  | limit:85 |  |  |  |  |  |
| 1 | DIMMA~F Temp | DIMMA~D Temp |  |  |  | P1-DIMMA1 Temp |  | DIMMA~D Temp |  |  |  |  |  |
| 2 | DIMMG~L Temp | DIMME~H Temp |  |  |  | P1-DIMMB1 Temp |  | DIMME~H Temp |  |  |  |  |  |
| 3 |  |  |  |  |  | P1-DIMMC1 Temp |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  | P1-DIMMD1 Temp |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  | P2-DIMME1 Temp |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  | P2-DIMMF2 Temp |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  | P2-DIMMG1 Temp |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  | P2-DIMMH1 Temp |  |  |  |  |  |  |  |

- Sever sensor(StoageDevice) 僅Quine有

| Server | Quine |
| --- | --- |
| 1 | AOC_SAS1 Temp(limit:105) |
| 2 | AOC_SAS2 Temp(limit:105) |
| 3 | HDD Temp Yes(limit:55) |

- Sever sensor(ASIC)

| Server | Quine | Maxwell | Lavoisier |
| --- | --- | --- | --- |
| 1 | AIOM_NIC1 Temp(limit:100) | AIOM_NIC1 Temp(limit:100) | AOC_NIC3 Temp(limit:100) |

- Sever sensor(CPU)

| Server | Quine | Maxwell | Davinci | Joule | Einstein | Newton | Bell | Lavoisier | Ohm | Galileo | Archmedies | Kepler | Inoue |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | CPU Temp(limit:100) | CPU_VRMIN Temp(limit:96) |  | limit: 100 |  | CPU1 Temp(limit:98) |  | CPU Temp(limit:96) |  |  |  | CPU1 Temp | CPU1 Temp |
| 2 | CPU_VRM0 Temp (limit:100) | CPU_VRMON Temp(limit:100) |  | CPU1 Temp |  | CPU2 Temp(limit:98) |  | CPU_VRMIN Temp(limit:100) |  |  |  | CPU2 Temp | CPU2 Temp |
| 3 | CPU_VRM1 Temp (limit:85) | CPU_VRMHV Temp(limit:100) |  | CPU2 Temp |  | PCH Temp(limit:95) |  | CPU_VRMON Temp(limit:100) |  |  |  |  |  |
| 4 |  |  |  |  |  | System Temp(limit:85) |  | CPU_VRMHV Temp(limit:100) |  |  |  |  |  |
| 5 |  |  |  |  |  | Peripheral Temp(limit:85) |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  | MB_10G Temp(limit:100) |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  | Vcpu1VRM Temp(limit:100) |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  | Vcpu2VRM Temp(limit:100) |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  | VmemABVRM Temp(limit:100) |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  | VmemEFVRM Temp(limit:100) |  |  |  |  |  |  |  |

- 問題與討論

  - Q: 要用哪些伺服器才可以穩定供應?

A: Quine/Davinci/Inoue/Kepler

    - Why:因為都有cpu temp、Inlet Temp、Fan RPM、Sever Power、PDU Mapping、Online，所以可以長時間收集

    - 用途: 當主要CPU Temp 、Inlet temp、redfish power Dataset

  - Q: 每個sever的sensor名稱、數量不同

A: 需要標準化，才能輸入到模型。(例如:Front Ambient/System/Board Inlet Temp: Inlet_Temp)

  - Q: 每個server廠牌、處理器、模型不同

A: 可以先同廠牌的server資料輸入至模型進行測試，再來測試不同廠牌/模型/處理器會有什麼影響

- Feature 定義

| 類別 | Feature | 定義 |
| --- | --- | --- |
| 溫度 | CPU Temp | 主要預測目標，也可當歷史輸入 |
| 溫度 | Inlet temp | 代表進入伺服器的環境溫度 |
| 功率 | redfish power | 代表伺服器負載造成的熱源 |
| 散熱 | Fan RPM | 代表散熱強度 |

- Field Guide

| Section | Field / Data Item | Meaning | Example | How to Fill |
| --- | --- | --- | --- | --- |
| Asset | Rack | Which rack contains the server | BMW Old-Rack | Read from asset detail page |
| Asset | U Position | Server physical location in rack | U37-U38 | Read from asset detail page |
| Collection | Redfish Data Available | Whether Redfish detail pages show telemetry | Yes / No / Unknown | Check Redfish information and data log tabs |
| Collection | PDU Outlet | Specific outlet connected to server | Outlet 10 | Read PDU socket block |
| Power | Redfish Power | Server power reported by BMC/Redfish | 243 W | Read power information / Redfish info tab |
| Power | PDU active_power | Outlet power measured by PDU | Outlet 10 active_power | Check InfluxDB or PDU dashboard |
| Thermal | CPU Temp | CPU temperature from Redfish | CPU1 70°C, CPU2 63°C | Read thermal sensor tab |
| Thermal | Inlet Temp | Server inlet temperature | 19°C | Read thermal tab |
| Cooling | Fan RPM | Fan speed reported by BMC | 5640 RPM | Read fan sensor tab |
| Workload | CPU Utilization | Host CPU usage from Node Exporter | 0% / Missing | Check performance metrics tab |
| Health | Health Status | Hardware health from Redfish | OK / Critical | Read overview tab |